## Design
Air core Inductors |  |  | 22.9824 | ID+T=D
Coil length B | 36 | 24 | 1.0443 | B/D |  | Build Factor | 1.11
Coil ID + barrier | 9.75 |  | 0.57576 | T/D
Coil thk T | 13.2324 |  | 11.5244 | K |  | Freq | Amps | Bmax | W/LB | w/lb*lb | Watts | AC Ohms | Rac/Rdc | Q | Dpen | D | M
Num turns N | 45 |  |  |  |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0.31304 | 205.6664 | 1.1233 | 0.10683 | 0.30316 | 1.1335
O.D. | 36.2148 |  |  |  |  | 1000 | 0 | 0 | 0 | 0 | 0 | 0.095138 | 62.5054 | 0.79428 | 0.15108 | 0.091112 | 1.0349
micro H L= | 513.5991 | L=K*D^2*N^2*10^-3/B |  |  |  | 500 | 0 | 0 | 0 | 0 | 0 | 0.027739 | 18.2246 | 0.56164 | 0.21366 | 0.025518 | 1.0088
[6 empty] | 100 | 0 | 0 | 0 | 0 | 0 | 0.0027314 | 1.7945 | 0.25117 | 0.47776 | 0.0011771 | 1.0004
[6 empty] | 10000 | 0 | 0 | 0 | 0 | 0 | 2.4821 | 1630.7189 | 2.5117 | 0.047776 | 2.4134 | 2.4901
[6 empty] | 20000 | 0 | 0 | 0 | 0 | 0 | 3.8342 | 2519.0442 | 3.5521 | 0.033782 | 3.7285 | 3.5604
[6 empty] | 420 | 0 | 0 | 0 | 0 | 0 | 0.020429 | 13.4221 | 0.51475 | 0.23312 | 0.018403 | 1.0062
DC Amps | 0 |  | AC Amps | 4000 |  | Cond Area | 2.8792
No Conductors | 1 |  | Thickness | 0.12 |  | Width | 24 |  | (Cond/(Cond+gap))^2
Cu=1,Alum=0 | 0 |  | A= | 11.4912 |  | Cond gap | 0.01 |  | 0.99917
No. Layers | 45 |  | MLT= | 72.2013 |  | Margin | 6
Layer Ins. | 0.01 |  | Cond Lgh= | 270.7548 | Ft. | LBS= | 913.629
No Sticks | 9 |  | Stk Thk | 0.75 |  | DC Ohms | 0.0015221 | at 75C |  | Round molds |  |  | 0.001244 | at 20C
Turns/layer | 1 |  | Duct Eff | 0.8 |  | I^2R= | 24353.1761 |  |  | 3 | 1
micro H | 512.6576 | L=.8*A^2*N^2/(6*A+9*C2+10*B4) |  |  |  | Eddy= | 36535.2304 |  |  | 3.5 | 1.5
L-L micfarads | 0.11205 |  |  |  |  | Total= | 60888.4065 | 60888.4065 |  | 5 | 2.5625
Ind micfarads | 0.00049148 |  |  |  |  | Surface= | 29636.0831 | 5376.4537 |  | 5.625 | 3.125
Res Freq Khz | 317.0672 |  | Target |  |  | W/SqIn= | 2.0545 | 11.325 |  | 9.375 | 4.625
IZ at 60 hz |  | 0.19327 | 0.2 |  |  | Temp Rise | 133.4235 | 522.7478 | [5 empty] | MLT per layer | 72.2013 |  |  | MLT per layer | 72.2013
Test current |  | 600 |  |  |  | AmpSqIn | 1389.2931 | [6 empty] | MLT adder | 1 |  |  | spacing between sticks | 2.5
Test volts @ AC amps |  | 115.964 | [11 empty] | winding height | 36 |  |  | sticks per layer | 28
Note: most coils are not round. Incease the ID by 1 for small coils and .5 for large when bars are used for leads. | [13 empty] | pieces per layer | 1 |  |  | no of layers with sticks | 9
This simulates actual micro H at the smaller ID. | [13 empty] | multiplier | 1.05 |  |  | total number of sticks | 252
[6 empty] | R @ 20C | 0.001244 | [6 empty] | square inches per layer | 2767.0083
hi pot | 50 kv |  |  |  |  | mH Nominal | 0.53052
est overload | [5 empty] | mH min | 0.47746
current | 30000 |  | watts= | 3424972.8647 |  | Fault/SQI | 10419.6985
seconds | 10 |  | W/sqin= | 115.5677 | [9 empty] | coil OD | 36.2148 |  |  | MLT per layer | 72.2013
temp rise | 142.7352 | [12 empty] | MLT adder | 1 |  |  | Keepback | 6
Adiabatic temp rise | 225.5595 | [12 empty] | winding height | 36 |  |  | num of layers | 45
| design guide rule of thumb | [12 empty] | pieces per wrap | 1 |  |  | pieces | 2
[14 empty] | multiplier | 1.05 |  |  | multiplier | 1.05
| 1.15 | 150 | 45 | 1.33 | 5.9725 | mils per layer | [7 empty] | square inches of wrap | 4338.3873 |  |  | square inches of PO | 81876.2493
​​26.4kV L-L (150kV BIL), 600A Continuous, 10kA Fault Current @ 1 Seconds, 1.1 Ohms, 60Hz, Aluminum, 200C Insulation System, Single Phase Current Limiting Reactor in a NEMA 3R Aluminum​ Enclosure R0 1/22/26 R1 1/29/26 - doubled sticks
[14 empty] | Mould ID | 9.25 |  |  | lead pad width | 5
[14 empty] | Mould OD | 9.75 |  |  | coil height | 36
[14 empty] | MLT | 29.8451 |  |  | pad outside coil | 0
[14 empty] | pieces of 1/32 redboard | 8 |  |  | pieces | 4
[14 empty] | mould above coil | 3.5 |  |  | multiplier | 1.05
[14 empty] | coil height | 36 |  |  | square inches of padding | 756
[14 empty] | mould below coil | 3
[14 empty] | multiplier | 1.05
[14 empty] | square inches of red board/FHT | 10654.7115
Note on H12: single cond.
Note on A34: B33 uses an empirical model with a fixed 1-hour thermal time constant, which assumes significant heat dissipation during the fault. This is reasonable for longer-duration overloads. B34 uses an adiabatic model (zero heat loss), which assumes all fault energy stays in the conductor. This is the conservative upper bound and more accurate for short-duration faults (seconds), where the coil has little time to dissipate heat. The true temperature will fall between these two values. For fault protection decisions, the adiabatic value (B34) is the safer reference.

## Layer 60
Air core Inductors |  |  | 15.6529 | ID+T=D
Coil length B | 34.5 | 24 | 1.5333 | B/D |  | Build Factor | 1.11
Coil ID + barrier | 12 |  | 0.23337 | T/D
Coil thk T | 3.6529 |  | 16.2353 | K |  | Freq | Amps | Bmax | W/LB | w/lb*lb | Watts | AC Ohms | Rac/Rdc | Q | Dpen | D | M
Num turns N | 60 |  |  |  |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0.017582 | 3.1773 | 0.28082 | 0.10683 | 0.0018144 | 1.0006
O.D. | 19.3058 |  |  |  |  | 1000 | 0 | 0 | 0 | 0 | 0 | 0.0086621 | 1.5653 | 0.19857 | 0.15108 | 0.00047114 | 1.0001
micro H L= | 596.6807 | L=K*D^2*N^2*10^-3/B |  |  |  | 500 | 0 | 0 | 0 | 0 | 0 | 0.0063374 | 1.1452 | 0.14041 | 0.21366 | 0.00012104 | 1
[6 empty] | 100 | 0 | 0 | 0 | 0 | 0 | 0.005567 | 1.006 | 0.062794 | 0.47776 | 5.0246e-06 | 1
[6 empty] | 10000 | 0 | 0 | 0 | 0 | 0 | 0.26212 | 47.3683 | 0.62794 | 0.047776 | 0.03864 | 1.0137
[6 empty] | 20000 | 0 | 0 | 0 | 0 | 0 | 0.90558 | 163.6491 | 0.88804 | 0.033782 | 0.13553 | 1.054
[6 empty] | 420 | 0 | 0 | 0 | 0 | 0 | 0.0061039 | 1.103 | 0.12869 | 0.23312 | 8.5877e-05 | 1
DC Amps | 0 |  | AC Amps | 600 |  | Cond Area | 0.71916
No Conductors | 1 |  | Thickness | 0.03 |  | Width | 24 |  | (Cond/(Cond+gap))^2
Cu=1,Alum=0 | 0 |  | A= | 7.8264 |  | Cond gap | 0.01 |  | 0.99917
No. Layers | 60 |  | MLT= | 49.175 |  | Margin | 5.25
Layer Ins. | 0.01 |  | Cond Lgh= | 245.875 | Ft. | LBS= | 207.2377
No Sticks | 2 |  | Stk Thk | 0.5 |  | DC Ohms | 0.0055337 | at 75C |  | Round molds |  |  | 0.0045225 | at 20C
Turns/layer | 1 |  | Duct Eff | 0.8 |  | I^2R= | 1992.1208 |  |  | 3 | 1
micro H | 589.0377 | L=.8*A^2*N^2/(6*A+9*C2+10*B4) |  |  |  | Eddy= | 20.7544 |  |  | 3.5 | 1.5
L-L micfarads | 0.092614 |  |  |  |  | Total= | 2012.8751 | 2012.8751 |  | 5 | 2.5625
Ind micfarads | 0.0010873 |  |  |  |  | Surface= | 6024.222 | 2719.6624 |  | 5.625 | 3.125
Res Freq Khz | 198.8752 |  | Target |  |  | W/SqIn= | 0.33413 | 0.74012 |  | 9.375 | 4.625
IZ at 60 hz |  | 0.22213 | 1.1 |  |  | Temp Rise | 31.2028 | 58.9526 | [5 empty] | MLT per layer | 49.175 |  |  | MLT per layer | 49.175
Test current |  | 600 |  |  |  | AmpSqIn | 834.3044 | [6 empty] | MLT adder | 1 |  |  | spacing between sticks | 2.5
Test volts @ AC amps |  | 133.2786 | [11 empty] | winding height | 34.5 |  |  | sticks per layer | 19
Note: most coils are not round. Incease the ID by 1 for small coils and .5 for large when bars are used for leads. | [13 empty] | pieces per layer | 1 |  |  | no of layers with sticks | 2
This simulates actual micro H at the smaller ID. | [13 empty] | multiplier | 1.05 |  |  | total number of sticks | 38
[6 empty] | R @ 20C | 0.0045225 | [6 empty] | square inches per layer | 1817.5892
hi pot | 34 kv |  |  |  |  | mH Nominal | 2.9178
est overload | [5 empty] | mH min | 2.6261
current | 10000 |  | watts= | 559131.9833 |  | Fault/SQI | 13905.0728
seconds | 2 |  | W/sqin= | 92.814 | [9 empty] | coil OD | 19.3058 |  |  | MLT per layer | 49.175
temp rise | 32.7655 | [12 empty] | MLT adder | 1 |  |  | Keepback | 5.25
AI temp rise | 44.4651 | [12 empty] | winding height | 34.5 |  |  | num of layers | 60
| design guide rule of thumb | [12 empty] | pieces per wrap | 1 |  |  | pieces | 2
[14 empty] | multiplier | 1.05 |  |  | multiplier | 1.05
| 1.15 | 150 | 60 | 1.33 | 4.0737 | mils per layer | [7 empty] | square inches of wrap | 2233.306 |  |  | square inches of PO | 65058.5172
​​26.4kV L-L (150kV BIL), 600A Continuous, 10kA Fault Current @ 1 Seconds, 1.1 Ohms, 60Hz, Aluminum, 200C Insulation System, Single Phase Current Limiting Reactor in a NEMA 3R Aluminum​ Enclosure
[14 empty] | Mould ID | 9.25 |  |  | lead pad width | 5
[14 empty] | Mould OD | 12 |  |  | coil height | 34.5
[14 empty] | MLT | 33.3794 |  |  | pad outside coil | 0
[14 empty] | pieces of 1/32 redboard | 44 |  |  | pieces | 4
[14 empty] | mould above coil | 3.5 |  |  | multiplier | 1.05
[14 empty] | coil height | 34.5 |  |  | square inches of padding | 724.5
[14 empty] | mould below coil | 3
[14 empty] | multiplier | 1.05
[14 empty] | square inches of red board/FHT | 63227.301
Note on H12: single cond.
Note on A34: B33 uses an empirical model with a fixed 1-hour thermal time constant, which assumes significant heat dissipation during the fault. This is reasonable for longer-duration overloads. B34 uses an adiabatic model (zero heat loss), which assumes all fault energy stays in the conductor. This is the conservative upper bound and more accurate for short-duration faults (seconds), where the coil has little time to dissipate heat. The true temperature will fall between these two values. For fault protection decisions, the adiabatic value (B34) is the safer reference.

## 800815 for ref
Air core Inductors |  |  | 16.0667 | ID+T=D
Coil length B | 17.4375 | 6.57 | 0.40892 | B/D |  | Build Factor | 1.11
Coil ID + barrier | 9.75 |  | 0.39315 | T/D
Coil thk T | 6.3167 |  | 7.7013 | K |  | Freq | Amps | Bmax | W/LB | w/lb*lb | Watts | AC Ohms | Rac/Rdc | Q | Dpen | D | M
Num turns N | 378 |  |  |  |  | 2000 | 0 | 0 | 0 | 0 | 0 | 73.9804 | 214.9447 | 1.9386 | 0.066026 | 1.4531 | 1.827
O.D. | 22.3834 |  |  |  |  | 1000 | 0 | 0 | 0 | 0 | 0 | 29.2846 | 85.0842 | 1.3708 | 0.093374 | 0.57141 | 1.277
micro H L= | 43234.9198 | L=K*D^2*N^2*10^-3/B |  |  |  | 500 | 0 | 0 | 0 | 0 | 0 | 9.6585 | 28.0622 | 0.96932 | 0.13205 | 0.184 | 1.0759
[6 empty] | 100 | 0 | 0 | 0 | 0 | 0 | 0.83031 | 2.4124 | 0.43349 | 0.29528 | 0.0096087 | 1.0031
[6 empty] | 10000 | 0 | 0 | 0 | 0 | 0 | 226.7012 | 658.6641 | 4.3349 | 0.029528 | 4.4613 | 4.3349
[6 empty] | 20000 | 0 | 0 | 0 | 0 | 0 | 311.1191 | 903.934 | 6.1305 | 0.020879 | 6.1214 | 6.1306
[6 empty] | 420 | 0 | 0 | 0 | 0 | 0 | 7.2144 | 20.9609 | 0.8884 | 0.14408 | 0.13573 | 1.0541
DC Amps | 0 |  | AC Amps | 95 |  | Cond Area | 0.045882
No Conductors | 1 |  | Thickness | 0.128 |  | Width | 0.365 |  | (Cond/(Cond+gap))^2
Cu=1,Alum=0 | 1 |  | A= | 8.0333 |  | Cond gap | 0 |  | 1
No. Layers | 21 |  | MLT= | 50.4749 |  | Margin | 5.25
Layer Ins. | 0.015 |  | Cond Lgh= | 1589.96 | Ft. | LBS= | 282.7709
No Sticks | 4 |  | Stk Thk | 0.75 |  | DC Ohms | 0.34418 | at 75C |  | Round molds |  |  | 0.28302 | at 20C
Turns/layer | 18 |  | Duct Eff | 0.8 |  | I^2R= | 3106.2552 |  |  | 3 | 1
micro H | 43266.2793 | L=.8*A^2*N^2/(6*A+9*C2+10*B4) |  |  |  | Eddy= | 2169.5397 |  |  | 3.5 | 1.5
L-L micfarads | 0.014383 |  |  |  |  | Total= | 5275.7949 | 5275.7949 |  | 5 | 2.5625
Ind micfarads | 0.00028848 |  |  |  |  | Surface= | 3290.6297 | 1300.9083 |  | 5.625 | 3.125
Res Freq Khz | 45.0494 |  | Target |  |  | W/SqIn= | 1.6033 | 4.0555 |  | 9.375 | 4.625
IZ at 60 hz |  | 16.3146 | 16 |  |  | Temp Rise | 109.4129 | 229.8763 | [5 empty] | MLT per layer | 50.4749 |  |  | MLT per layer | 50.4749
Test current |  | 95 |  |  |  | AmpSqIn | 2070.5287 | [6 empty] | MLT adder | 1 |  |  | spacing between sticks | 2.5
Test volts @ AC amps |  | 1549.8902 | [11 empty] | winding height | 17.4375 |  |  | sticks per layer | 20
Note: most coils are not round. Incease the ID by 1 for small coils and .5 for large when bars are used for leads. | [13 empty] | pieces per layer | 1 |  |  | no of layers with sticks | 4
This simulates actual micro H at the smaller ID. | [13 empty] | multiplier | 1.05 |  |  | total number of sticks | 80
[6 empty] | R @ 20C | 0.28302 | [6 empty] | square inches per layer | 942.4736
hi pot | 34 kv |  |  |  |  | mH Nominal | 42.4413
est overload | [5 empty] | mH min | 38.1972
current | 240 |  | watts= | 33671.5555 |  | Fault/SQI | 5230.8095
seconds | 5 |  | W/sqin= | 10.2326 | [9 empty] | coil OD | 22.3834 |  |  | MLT per layer | 50.4749
temp rise | 110.0823 | [12 empty] | MLT adder | 1 |  |  | Keepback | 5.25
AI temp rise | 112.8222 | [12 empty] | winding height | 17.4375 |  |  | num of layers | 21
| design guide rule of thumb | [12 empty] | pieces per wrap | 1 |  |  | pieces | 2
[14 empty] | multiplier | 1.05 |  |  | multiplier | 1.05
| 1.15 | 150 | 21 | 1.33 | 16.458 | mils per layer | [7 empty] | square inches of wrap | 1305.8136 |  |  | square inches of PO | 23372.4123
Q38459A: 13200V L-L (150kV BIL), 16.00 Ohms +\- 10% at 25C, 95A Continuous Neutral, 240A Fault Current at 5 Seconds Max Duration, 60Hz, 150C Rise, Copper, 200C Insulation System, Single Phase, Neutral Grounding Reactor w/C20 200:5 Current Transformer in NEMA 3R Enclosure Bottom Cable Entry, 1/4" x 1 Copper Terminal
[14 empty] | Mould ID | 9.25 |  |  | lead pad width | 5
[14 empty] | Mould OD | 9.75 |  |  | coil height | 17.4375
[14 empty] | MLT | 29.8451 |  |  | pad outside coil | 0
[14 empty] | pieces of 1/32 redboard | 8 |  |  | pieces | 4
[14 empty] | mould above coil | 3.5 |  |  | multiplier | 1.05
[14 empty] | coil height | 17.4375 |  |  | square inches of padding | 366.1875
[14 empty] | mould below coil | 3
[14 empty] | multiplier | 1.05
[14 empty] | square inches of red board/FHT | 6001.1096
Note on H12: single cond.
Note on A34: B33 uses an empirical model with a fixed 1-hour thermal time constant, which assumes significant heat dissipation during the fault. This is reasonable for longer-duration overloads. B34 uses an adiabatic model (zero heat loss), which assumes all fault energy stays in the conductor. This is the conservative upper bound and more accurate for short-duration faults (seconds), where the coil has little time to dissipate heat. The true temperature will fall between these two values. For fault protection decisions, the adiabatic value (B34) is the safer reference.

## Reactor Stats
Eng. Design | Mould/ Tube ID | Winding ID | Winding OD | Winding Height | Coil Height | Margin | Turns | micro Henries | ohms | copper weight | System Volts/Class | BIL | Continuous Amps | Fault Amps | Seconds | CT? | W/SqI | Ohms check
A800831 | 3.5 | 3.875 | 13.875 | 13.875 | 3.375 | 5.25 | 151.125 | 3500 | 1.32 | 70 | 15000 | 95 | 90 | 978 | 10 | N | 1.1041
A800830 | 9.25 | 9.75 | 25.625 | 25.125 | 14.875 | 5.125 | 563.5 |  | 29 | 1044 | 12470 | 95 | 130 | 2250 | 10 | Y | 1.2366
A800829 | 9.25 | 9.75 | 27.5 | 46 | 27 | 9.5 | 48 | 400 |  | 778 | 34500 | 150 | 1250 | 30000 | 3 | N | 0.2579
A800828 | 3.5 | 3.875 | 11.625 | 16.1875 | 5.625 | 5.25 | 160 | 2810 | 1.06 |  | 15000 | 95 | 81 | 1337 | 10 | N | See 800821
A800827 | 9.25 | 9.75 | 15 | 16.375 | 5.875 | 5.25 | 287 | 22520 | 8.5 | 103.1 | 15000 | 95 |  | 456 | 10 | Y | 0.6723
A800826 | 8 | 8.25 | 12.375 | 44.375 | 41.125 | 1.625 | 128 |  | 0.09 | 690 | 4160 | 45 | 269 | 4780 | 10 | N | 0.3985
A800824 | 4.625 | 5.125 | 10.5 | 22.375 | 16.875 | 2.75 | 92 |  | 0.21 | 188 | 4160 | 60 | 250 | 6000 | 10 | N | 0.3116
A800822 | 5.5 | 5.875 | 11.25 | 15.125 | 11.125 | 2 | 48 |  | 0.09 | 145 | 4160 | 45 | 269 | 4780 | 10 | Y | 0.171
A800821 | 3.5 | 3.875 | 11.625 | 16.1875 | 5.625 | 5.25 | 160 | 2828.5457 | 1.0678 | 72 | 15000 | 95 | 81 | 1337 | 5 | N | 0.4684 | 1.0663
A800820 | 9.25 | 9.75 | 20.0171 | 20.9375 | 9.75 | 5.25 | 330 | 26258.8542 | 9.9009 | 360.9748 | 15000 | 150 | 140 | 380 | 5 | Y | 1.2413 | 9.8994
A800819 (815) | 9.25 | 9.75 | 22.3834 | 17.4375 | 6.57 | 5.25 | 378 | 43266.2793 | 16.3146 | 282.7709 | 15000 | 150 | 95 | 250 | 5 | Y | See 800815 | 16.311
A800818 | 3 | 3.5 | 6.8442 | 16.125 | 5.058 | 5.25 | 60 | 247.6926 | 0.093886 | 26.0635 | 15000 | 95 | 88 | 1838 | 10 | Y | 0.2788 | 0.093378
A800817 | 9.25 | 9.75 | 20.0659 | 24.0625 | 13.14 | 5.25 | 720 | 107392.8338 | 40.4907 | 499.7666 | 15000 | 95 | 100 | 200 | 2 | N | 1.6501 | 40.4861
A800816 | 9.25 | 9.75 | 20.0171 | 21.5625 | 10.4 | 5.25 | 352 | 28954.8424 | 10.9173 | 385.0397 | 15000 | 150 | 140 | 360 | 5 |  | 1.2504 | 10.9157
A800815 | 9.25 | 9.75 | 22.3834 | 17.4375 | 6.57 | 5.25 | 378 | 43266.2793 | 16.3146 | 282.7709 | 15000 | 150 | 95 | 240 | 5 |  | 1.6033 | 16.311
A800814 | 3 | 3.5 | 6.7697 | 12.375 | 1.6577 | 5.1875 | 31 | 108.5796 | 0.042224 | 6.4549 | 13800 | 95 | 100 | 325 | 10 |  | 0.8309 | 0.040934
A800813 | 9.25 | 9.75 | 25.9531 | 25.125 | 13.87 | 5.25 | 551 | 74595.9245 | 28.1231 | 1032.5415 | 15000 | 95 | 121 | 2100 | 5 |  | 1.179 | 28.122
A800812 | 5 | 5.625 | 11.4812 | 26.875 | 7.7971 | 9.5 | 2060 | 496255.0422 | 187.4221 | 72.7712 | 25000 | 150 | 2.6 | 64 | 10 |  | 0.063 | 187.0837
A800811 | 6 | 6.5 | 15.6516 | 19.173 | 7.36 | 5.25 | 78 | 1027.8431 | 0.38759 | 216.5932 | 15000 | 95 | 450 | 450 | 10 |  | 1.7604 | 0.38749
A800810 | 4.625 | 5 | 7.958 | 5.161 | 3.672 | 0.5 | 42 | 221.0459 | 0.083775 | 22.7762 | 600 | 10 | 36 | 1500 | 10 |  | 0.8086 | 0.083332
A800809 | 4.625 | 5 | 9.6846 | 13.7325 | 7.349 | 2.75 | 102 | 1008.6036 | 0.38061 | 88.0854 | 4160 | 60 | 173 | 2086 | 10 |  |  | 0.38023
A800808 | 4.625 | 5 | 11.7626 | 14.9375 | 4.226 | 5.25 | 198 | 5696.4125 | 2.1502 | 67.1888 | 13800 | 95 | 68 | 729 | 10 |  |  | 2.1475
A800806 | 4.625 | 5 | 11.1574 | 14.9375 | 4.128 | 5.25 | 240 | 8183.2583 | 3.0899 | 57.1298 | 12470 | 95 | 58 | 582 | 10 |  |  | 3.085
A800805 | 5 | 5.5 | 14.2842 | 16.43 | 13.17 | 1 | 288 | 8448.9529 | 3.1858 | 353.2659 | 13800 | 95 | 50 | 2500 | 10 |  |  | 3.1852
A800804 | 3.5 | 3.875 | 9.8828 | 12.305 | 5.681 | 3 | 174 | 2814.4832 | 1.0624 | 69.3139 | 12470 | 95 | 90 | 1207 | 10 |  |  | 1.061
A800803 | 5 | 5.625 | 11.365 | 23.6 | 8.19 | 7.5 | 900 | 91408.8436 | 34.4787 | 137.2099 | 15000 | 125 | 8.4 | 280.3 | 10 |  |  | 34.4603
A800802 | 7.25 | 7.75 | 11.4148 | 11.695 | 5.712 | 2.75 | 123 | 2821.2677 | 1.0649 | 69.2197 | 13800 | 60 | 81 | 1337 | 10 |  |  | 1.0636
A800801 | 5 | 5.625 | 10.3707 | 23.625 | 4.542 | 9.5 | 1079 | 168107.0303 | 63.6142 | 35.6422 | 13200 | 150 | 4.4 | 110 | 10 |  |  | 63.3749
A800800 | 8.625 | 9.375 | 15.0771 | 18.7325 | 6.198 | 6 | 275 | 18771.9906 | 7.0824 | 106.6247 | 12470 | 95 | 37.1 | 926 | 10 |  |  | 7.0769
A800799 | 8.5 | 9.375 | 23.8832 | 28.0625 | 8.6802 | 9.5 | 391 | 42290.7191 | 15.9455 | 412.2172 | 15000 | 150 | 100 | 1178 | 5 |  |  | 15.9432
A800798 | 4.625 | 5 | 10.776 | 9.6875 | 3.9627 | 2.75 | 221 | 6913.2688 | 2.6103 | 55.2634 | 13200 | 60 | 57 | 702 | 10 |  |  | 2.6062
A800795 | 7.25 | 7.75 | 11.2952 | 11.875 | 5.78 | 2.75 | 110 | 2267.9731 | 0.84249 | 70.0415 | 13800 | 60 | 81 | 1623 | 10 |  |  | 0.85501
A800789 |  | 34.5 | 41.0803 | 4.5 | 3.25 | 0.625 | 14 | 318.9421 | 0.12026 | 340.2507 |  |  | 100 | 16000 | 0.1 |  |  | 0.12024
A800788 | 4.625 | 5 | 11.1774 | 9.9375 | 4.128 | 2.75 | 256 | 9320.5999 | 3.5187 | 61.0137 | 13200 | 60 | 55 | 616 | 10 |  |  | 3.5138
A800787 | 7.875 | 8.375 | 19.7082 | 20.5 | 14.175 | 2.875 | 560.5 | 54727.2481 | 20.6367 | 177.6572 | 13800 | 60 | 100 | 600 | 10 |  |  | 20.6317
A800785 | 3.5 | 3.875 | 11.8612 | 12.4375 | 5.964 | 3 | 164 | 2841.1094 | 1.0743 | 25.9566 | 12470 | 95 | 90 | 1207 | 10 |  |  | 1.0711
A800784 | 9 | 9.04 | 12.5464 | 11.375 | 5.475 | 2.75 | 118 | 3270.7056 | 1.2357 | 52.6923 | 12470 | 60 | 87 | 1038 | 10 |  |  | 1.233
A800783 | 9 | 9.04 | 12.8368 | 11.75 | 5.84 | 2.75 | 141 | 4558.7427 | 1.7214 | 63.8099 | 12470 | 60 | 80 | 765 | 10 |  |  | 1.7186
A800777 | 9 | 9.04 | 25.8105 | 21.6875 | 8.3028 | 6.5 | 460 | 60942.8489 | 22.9773 | 507.5696 | 13800 |  | 100 | 1200 | 1
A800775 | 11.5 | 12.25 | 17.1209 | 12.0625 | 10.565 | 0.625 | 300 | 23743.2837 | 8.9556 | 178.1607 | 11000 | 110 | 464 | 1160
A800764 |  | 4.875 | 6.6483 | 2.25 | 2.1762 | 0 | 615 | 54903.9922 | 23.6729 | 2.8838 | 25000 |  | 1
A800752 | 8.125 | 9 | 22.9798 | 17.75 | 14.96 | 1 | 360 | 26285.3786 | 9.9123 | 364.7366 | 15000 |  | 100 | 1200 | 2